DEMAND.EXE

ELECTRICAL DESIGN SOFTWARE

Residential Electrical Reports. Demand 2.0

DEMAND.EXE Documentation

(c) Copyright 1992-1993 Electrical Design Software

Licensed Material. All Rights Reserved.

����������  ��������       ������

���    ��   ���    �     ��    ��

���     �   ���     �   ��      �

���         ���     ��  ��

���  �      ���     ��  ���

���  �      ���     ��   ���

������      ���     ��     ���

���  �      ���     ��       ���

���  �      ���     ��        ���

���         ���     ��         ��

���     �   ���     �   �      ��

���    ��   ���    �    ��    ��

����������  ��������      ������

ELECTRICAL DESIGN SOFTWARE

12 Vassar Drive

Pelham, NH 03076

Phone or Fax: (603) 893-9008

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

TABLE OF CONTENTS                                          PAGE

~~~~~~~~~~~~~~~~~                                          ~~~~

Introduction ............................................... 1

Definition of Shareware .................................... 1

Disclaimer - Agreement ..................................... 2

What is DEMAND 2.0 ......................................... 2

System Requirements ........................................ 3

General Overview ........................................... 3

Files ...................................................... 3

Starting the Program ....................................... 3

Special Keys ............................................... 3

General Overview of Main Menu Selection .................... 4

Pop-Up Calculator .......................................... 5

Each Data Entry Field Explained ............................ 5-8

Produce Reports ............................................ 9

Data Base .................................................. 9

Command Buttons ............................................ 10

Service Schedule ........................................... 10

Demo Reports ............................................... 11-13

Help System ................................................ 14

Support .................................................... 15

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

I N T R O D U C T I O N

Electrical Design Software is a New Hampshire based company

that was established in 1992.  Our organization's primary objective

is to produce quality software, for the Electrical Industry, at a

reasonable price.

Demand 2.0 requires no special computer knowledge, and is

designed to accommodate both the amateur and professional user.

Context Sensitive Help Screens have been programmed into this

application in order for you the, user, to continue working

quickly and efficiently.

Most importantly, here at Electrical Design Software, YOUR

comments are considered essential, for the development of future

software products.  With your input we can design programs that

will accommodate the electrical profession and other specialized

fields.

DEFINITION OF SHAREWARE

Shareware distribution gives users a chance to try software

before buying it.  If you try a Shareware program and continue

using it, you are expected to register. Individual programs differ

on details -- some request registration while others require it,

some specify a maximum trial period.  With registration, you get

anything from the simple right to continue using the software to

an updated program with printed manual.

Copyright laws apply to both Shareware and Commercial

software, and the copyright holder retains all rights, with a

few specific exceptions as stated below. Shareware authors are

accomplished programmers, just like commercial authors, and the

programs are of comparable quality. (In both cases, there are

good programs and bad ones!) The main difference is in the method

of distribution. The author specifically grants the right to copy

and distribute the software, either to all and sundry or to a

specific group. For example, some authors require written

permission before a commercial disk vendor may copy their

Shareware.

Shareware is a distribution method, not a type of software.

You should find software that suits your needs and pocketbook,

whether it's commercial or Shareware. The Shareware system makes

fitting your needs easier, because you can try before you buy.

And because the overhead is low, prices are low also. Shareware

has the ultimate money-back guarantee -- if you don't use the

product, you don't pay for it.

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE    Page 1

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

DISCLAIMER - AGREEMENT

Users of Demand 2.0 must accept this disclaimer of warranty:

Demand 2.0 is supplied as is.  The author disclaims all warranties,

expressed or implied, including, without limitation, the warranties

of merchantability and of fitness for any purpose. The author

assumes no liability for damages, direct or consequential, which

may result from the use of Demand 2.0.

Demand 2.0 is a "Shareware Program" and is provided at no

charge to the user for evaluation.  Feel free to share it with

your friends, but please do not give it away altered or as part

of another system.  The essence of "user-supported" software is

to provide personal computer users with quality software without

high prices, and yet to provide incentive for programmers to

continue to develop new products.  If you find this program

useful and find that you are using Demand 2.0 and continue to use

Demand 2.0 after a reasonable trial period, you must make a

registration payment of *$39.00 to Electrical Design Software.

The *$39.00 registration fee will license one copy for use on

any one computer at any one time.  You must treat this software

just like a book. An example is that this software may be used

by any number of people and may be freely moved from one computer

location to another, so long as there is no possibility of it

being used at one location while it's being used at another. Just

as a book cannot be read by two different persons at the same time.

Commercial users of Demand 2.0 must register and pay for their

copies of Demand 2.0 within 30 days of first use or their license

is withdrawn. Site-License arrangements may be made by contacting

Electrical Design Software.

Anyone distributing Demand 2.0 for any kind of remuneration

must first contact Electrical Design Software at the address listed

for authorization. This authorization will be automatically granted

to distributors recognized by the (ASP) as adhering to its guidelines

for shareware distributors, and such distributors may begin offering

Demand 2.0 immediately (However Electrical Design Software must still

be advised so that the distributor can be kept up-to-date with the

latest version of Demand 2.0).

You are encouraged to pass a copy of Demand 2.0 along to your

friends for evaluation.  Please encourage them to register their

copy if they find that they can use it.  All registered users will

receive a copy of the latest version of the Demand 2.0.

WHAT IS DEMAND 2.0

Electrical Design Software designed Residential Electrical Reports

Demand 2.0 to be a user friendly program.  This application produces

professional customized reports for the demand calculation on new or

existing single dwellings.

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE    Page 2

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

SYSTEM REQUIREMENTS

Demand 2.0 requires the following hardware and/or software to operate:

1.  450K memory - 286 or higher CPU,

2.  IBM(R) PC/XT/AT or true "compatible" running MS-DOS or PC-DOS,

Operating System Version 3.1 or higher,

3.  One high-density floppy-disk drive or a hard disk drive (hard,

disk recommended)

4.  Use of mouse is optional.

-----------------------------------------------------------------

GENERAL OVERVIEW

. Context Sensitive Help as well as a Hyper-Text Help System.

. Data Base of records.

. Reporting to an ASCII File or Printer Ports LPT1 thru LPT3.

. Pop-up calculator.

. Automatically adjusts for a color or monochrome monitor.

-----------------------------------------------------------------

FILES

You should have the following files for the demand 2.0 program:

1.  Demand.exe      Main program.

2.  Demand.mdb      Data base file will be created on first start.

3.  Demand.hlp      Help screens.

4.  Demand.doc      Documentation.

5.  Feedback.doc    Program feedback.

6.  Isampack.exe    Utility to pack data file. (IN REG. VERSION).

7.  Isamrepr.exe    Utility to repair a damaged data file. (IN REG. VERSION).

-----------------------------------------------------------------

STARTING THE PROGRAM

To Start the Main Program Type  "DEMAND"  + press ENTER.

-----------------------------------------------------------------

SPECIAL KEYS

Demand 2.0 uses the following operating functions.

1.   ENTER or TAB  -  Advance forward.

2.   SHIFT + TAB   -  Move backwards.

3.   ALT           -  Activate the top Menu.

4.   ALT + HOT KEY -  Will menu item or command button.

5.   ESC           -  Move out of the program.

6.   Navigation    -  Up or down arrows keys.

7.   Page up       -  When at the customer name, page up will

move to the next record.

8.   Page down     -  When at the customer name, page down will

move to the previous record.

9.   Mouse         -  Select any field or button.

10.  F1            -  Context Help.

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE    Page 3

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

GENERAL OVERVIEW OF THE MAIN MENU SELECTIONS

REPORTS TO SCREEN

General to Screen .........  Send General Report to the screen.

Optional to Screen ........  Send Optional Report to the screen.

Existing to Screen ........  Send report for existing to screen.

REPORTS TO FILE OR PRINT

Long Print File ...........  Include Service Information in report.

Short Print File ..........  Send report only.

Long Print File Existing  .  Include service information in report.

Short Print File Existing .  Existing report only.

Print Field Form ..........  Print a form for field use.

DATA BASE

Index on City .............  Index records on the City Field.

Index on State ............  Index records on the State Field.

Index on Zip ..............  Index records on the Zip Field.

Index on Name .............  Index records on the Name Field.

Goto First ................  Make the first record the current record.

Goto Last .................  Make the Last record current.

Create New Record .........  Create a new record.

Update ....................  Update the current record.

Delete ....................  Delete the current record.

Previous ..................  Move to the previous record.

Next ......................  Move to the next record.

Find ......................  Bring up a search screen.

HELP

Contents ..................  Various help hyper-link topics.

Search ....................  Sort the help links in order.

Special Keys ..............  Screen navigation and functions.

Using Help ................  Explains about the help system.

About .....................  Information about this program.

QUIT

Quit ......................  Exit the program.

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE    Page 4

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

POP-UP CALCULATOR

Bring up a pop-up calculator that can add, subtract, multiply,

divide and do percents. With the mouse you can move the calculator

around. With the mouse cursor on the top of the calculator, press

the left mouse button and drag to a new screen location.

% - for percent.

/ - for divide.

* - for multiply.

- - for subtract.

+ - for addition.

c - to clear.

ce - clear last entry.

To remove the calculator press one of these listed below:

1.    Press ESC,

2.    Click the exit button on the calculator,

3.    Click the mouse on the background screen.

-----------------------------------------------------------------

EACH DATA ENTRY FIELD EXPLAINED

SQUARE FEET

Enter the square feet of floor area from the outside dimensions of

the building. The computed floor area shall not include open

porches, garages, or unused or unfinished spaces not adaptable for

future use.

Enter the living space.

REF: 220-3(b), 220-11, tables 220-3(b), 220-11

-----------------------------------------------------------------

SMALL APPLIANCE

Enter the quantity of 20 ampere, two wire, small appliance branch

circuits.

REF: 220-4(b), 220-16(a), 220-11, table 220-11

-----------------------------------------------------------------

LAUNDRY

Enter the quantity of 20 ampere, two wire, laundry branch circuits.

REF: 220-4(c), 220-16(b), 220-11, table 220-11

-----------------------------------------------------------------

HEATING

Enter the total wattage of the heating system.

In the case of a heat pump, if supplementary heat is not on at the

same time as the heat pump the smaller load need not be added to

the total.

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 5

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

ELECTRIC HEAT

Put an X in the box if:

~~~~~~~~~~~~~~~~~~~~~~~

1.  The heat is electric.

Do not put an X in the box if:

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

1.  The heat is not electric. This is used for the Optional

Calculation Method to determine if the heating load can be

calculated at 65 percent of the nameplate rating(s) of electric

space heating, if less then four separately controlled units.

-----------------------------------------------------------------

CONTINUOUS

Put an X in the box if:

~~~~~~~~~~~~~~~~~~~~~~~

1.  The heat is electric and the usual load is expected to be

continuous at the full nameplate value.

2.  The heating is not continuous, however, it is a heat pump

with the compressor load larger than the Supplemental load.

REF: Table 220-30(1)

CONTINUOUS = A load where the maximum current is expected to

continue for three hours or more.

REF: Article 100

NOTE: Table 220-30 States 100% of the nameplate ratings of electric

thermal storage and other heating systems where the usual load is

expected to be continuous at the full nameplate value.

REF: 220-30.

-----------------------------------------------------------------

FOUR OR MORE

Put an X in the box if: The heat is electric and is four or more

separately controlled units. This is used for the Optional

Calculation Method to determine if the heating load can be

calculated at 40 percent of the nameplate rating(s) of electric

space heating for four or more separately controlled units.

REF: 220-30.

-----------------------------------------------------------------

COOLING

Enter the total wattage of the cooling system. This value will also

be compared against the <Motor> loads of the fixed appliance

schedule to determine 25% of the largest motor.

REF: 220-21

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 6

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

DRYER

Enter the wattage of the electric dryer. For the general method if

an electric dryer is present the minimum demand load is 5000 watts.

For the optional method the dryer is calculated at nameplate.

REF: 220-18

-----------------------------------------------------------------

COOKING

Enter up to three electric ranges or cooking appliances. The

minimum wattage is 1751 to a maximum of 12,000. The program will

automatically classify each category according to column A,B or C

and apply the demand factors accordingly.

REF: 220-19

-----------------------------------------------------------------

FIXED APPLIANCE

Enter the fastened in place fixed appliances that are wattage

loads, such as water heater, dishwasher, etc.

REF: 220-17, 430-24, 430-25, 430-26

-----------------------------------------------------------------

FASTENED IN PLACE MOTOR APPLIANCES

Enter the name, volts and amps for the fixed appliances that are

motor loads, such as well pump, compactor, vent fan, disposal, pool

motor, etc. This group will be compared with each other as well as

the cooling load to determine 25% of the largest motor.

REF: 220-17, 430-24, 430-25, 430-26

-----------------------------------------------------------------

Table 430-148 Full-Load Currents in Amperes

Single-Phase Alternating-Current Motors

��������������������������������������������������������

HP         115v         200v         208v         230v

��������������������������������������������������������

1/6        4.4          2.5          2.4          2.2

1/4        5.8          3.3          3.2          2.9

1/3        7.2          4.1          4.0          3.6

1/2        9.8          5.6          5.4          4.9

3/4       13.8          7.9          7.6          6.9

��������������������������������������������������������

1          16            9.2          8.8          8

1�         20           11.5         11           10

2          24           13.8         13.2         12

3          34           19.6         18.7         17

��������������������������������������������������������

5          56           32.2         30.8         28

7�         80           46           44           40

10         100           57.5         55           50

��������������������������������������������������������

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 7

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

CUSTOMER INFOMATION

The Name, City, State & Zip code fields can be indexed. When

you go through the various records they will be displayed in

alphabetical order based on the indexed field. The name field is

the default index field.

-----------------------------------------------------------------

NOTE

This field will hold information up to 72 characters long

and is located directly under the city. When printing <Reports>

this field will print directly below the customer city.

Example:  After installing the service, a report could be produced

with a heading like:

Frank & Mary Smith

33 Peace Road

Hudson, NH 12345

Courtesy of ABC Electrical contractor 1-(234) 567-8901

-----------------------------------------------------------------

SERVICE REQUEST #

This is the number that is issued from the local utility company to

reference a specific service or project.

-----------------------------------------------------------------

SERVICE INFORMATION, EXAMPLES OF USE

Panel...... Square D 200 amp, 40 circuit surface main breaker.

Entrance... 4/0 AL conductor type XHHW in 2" PVC.

Grounding.. One 5/8" X 8' rod in cellar under panel #4 cu.

Report 1... 155' run from pole 24-17 along driveway.

Report 2... Granite State Electric Utility Co. (603)-898-9798

Report 3... 15 spare circuits as of 3/12/93.

Report 4... Lot #14

Report 5...

Report 6... Ran spare 2" PVC in trench for future fiber

Report 7... Optics cable as per owners request.

This will print on the reports when the long report is selected

-----------------------------------------------------------------

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 8

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

PRODUCE REPORTS FOR THE FOLLOWING

1. The General or Optional method for a new service.

2. The Optional method for an existing service.

3. Long reports have the service information attached.

4. Short reports have the calculation only.

REPORTS CAN GO TO

1. Disk via an ASCII file that you can edit.

2. Go to printer port LPT1 thru LPT3.

REPORT NOTES

1. When sending a report to a file you may replace an existing file

or append to an existing file.

2. When sending a report to the printer you may produce from 1 to

10 copies.

-----------------------------------------------------------------

DATA BASE

All records can be saved to disk in a data base file named

demand.mdb. The data base will first show records on an ascending

order based on the name field first.

Name  =  Name  -> City -> State

City  =  City  -> Name -> State

State =  State -> Name -> City

Zip   =  Zip   -> Name -> City

Example: The name index will sort based on the name, then as a

second index on city, and lastly on state.

-----------------------------------------------------------------

DATABASE REPAIR UTILITY

ISAMPACK purges records marked for deletion and recovers disk space

formerly used by deleted records in 32K blocks.

Syntax     ISAMPACK  DEMAND.MDB

-----------------------------------------------------------------

DATABASE PACKING UTILITY

ISAMREPR recovers databases that become corrupted.  It recreates

them by systematically evaluating every table and index and using

every piece of internally consistent information in the file.

Syntax     ISAMREPR  DEMAND.MDB

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 9

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

COMMAND BUTTONS

New Rec....... Create a new record.

Update........ Update the current record. When a record is changed

in any way, a message will ask if the program can

update the record for you before you exit.

Delete........ Delete the current record.

Previous...... Move to the previous record in the indexing

sequence.

Next.......... Move to the next record in the indexing sequence.

Find.......... Find a specific record. The search will take place

on the field that is the current index.

Calc.......... Bring up a pop up calculator.

Information... Toggle the service information screen.

Exit.......... Exit the program.

Esc........... The Esc button will move out of the program.

-----------------------------------------------------------------

SERVICE SCHEDULE

Conductor Types and Sizes

RH-RHH-RHW-THHW-THW-THWN-THHN-XHHW-USE

���������������������������������������������������������

Aluminum or

Copper              Copper-Clad AL        Rating in Amps

���������������������������������������������������������

AWG                     AWG

4                       2                    100

3                       1                    110

2                     1/0                    125

1                     2/0                    150

1/0                     3/0                    175

2/0                     4/0                    200

3/0                     250 kcmil              225

4/0                     300 kcmil              250

250 kcmil               350 kcmil              300

350 kcmil               500 kcmil              350

400 kcmil               600 kcmil              400

���������������������������������������������������������

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 10

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

GENERAL METHOD OF CALCULATION REPORT FOR A SINGLE DWELLING UNIT

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Sparky Conductor

12 High Volt Ave

Ampere, New Hampshire 12345

This is the location for the first note from the customer section

This is the location for the second note from the customer section

April 12, 1993 11:54 AM

Square Footage is  1800  X  3va .............   5400

Small Appliance Circuits is 5  X  1500va.....   7500

Laundry Circuits is 1  X  1500va ............   1500

======

Total ......................................:  14400

FIRST 3000 of the Small Appliance Total at 100% is ...    3000

Wattage from 3001 Watts to 120,000 Watts at 35% is ...    3990

======

6990

Net Lighting and Small Appliance Demand Total .................:   6990

Larger of the Heating or Cooling Load is the Heating Load at ...   7500

Electric Dryer Load is 5000  for a Demand Load of ..............   5000

Range) 12000   Cook 2) 5000    Cook 3) 3500   = Demand Load of..  13525

Fixed Appliance Motor Schedule

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

MOTOR                       VOLTS      AMPS      WATTS

~~~~~                       ~~~~~      ~~~~      ~~~~~

Pool                          240       7.3       1752

Fan                           120       5.5        660

Pump                          120       5.0        600

Fixed Appliance Wattage Schedule

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Appliance                   Watts

~~~~~~~~~                   ~~~~~

Water Heater                 4500

Dishwasher                   1500

Fixed Appliance Total =   9012 x 75%  = Demand Load of.........    6759

Demand Load for 25% of the Largest Motor ......................     438

======

Total Demand Load in Watts ...................................:   40212

System voltage:                       120/240

Computed Demand Load in Watts .......   40212

Computed Demand Load in KW ..........      40

Minimum Calculated Service Size =   40212  Watts � 240 Volts =  168 Amps

Service Information

~~~~~~~~~~~~~~~~~~~

Service Request #.. NH10355

Square D 200 Amp 40 Cir Main Breaker

4/0 AL Type XHHW in 2" PVC

#6 to Copper Ground Rod & Water Piping

18 - Spare Breakers

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 11

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

OPTIONAL METHOD OF CALCULATION REPORT FOR A SINGLE DWELLING UNIT

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Sparky Conductor

12 High Volt Ave

Ampere, New Hampshire 12345

This is the location for the first note from the customer section

This is the location for the second note from the customer section

April 12, 1993 11:54 AM

3va Per Square Foot X  1800 Square Feet ...........    5400

1500va Per Small Appliance Circuit X  5 Circuits ..    7500

1500va Per Laundry Circuit X  1 Circuits ..........    1500

Electric Range ....................................   12000

Cooking Unit Two ..................................    5000

Cooking Unit Three ................................    3500

Electric Dryer ....................................    5000

Water Heater            ...........................    4500

Dishwasher              ...........................    1500

Pool                    ...........................    1752

Fan                     ...........................     660

Pump                    ...........................     600

======

Total Other Load .................................:   48912

First 10,000 at 100%:                                 10000

Remainder at 40% .................................    15565

~~~~~~

Calculated Total of Other Load For New Dwelling...    25565

Larger of Heat or A/C = Cool for a Demand Load ....    4500

======

Total Load:                                           28565

Minimum Calculated Service Size =  28565 Watts � 240 Volts =  119 Amps.

Service Information

~~~~~~~~~~~~~~~~~~~

Service Request #.. NH10355

Square D 200 Amp 40 cir Main Breaker

4/0 AL Type XHHW in 2" PVC

#6 to Copper Ground Rod & Water Piping

Service Lateral is from Pole #2733

Along Driveway to left of Garage

Total Distance = 155'

18 - Spare Breakers

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 12

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

OPTIONAL METHOD CALC REPORT FOR AN EXISTING SINGLE DWELLING UNIT

~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~

Sparky Conductor

12 High Volt Ave

Ampere, New Hampshire 12345

This is the location for the first note from the customer section

This is the location for the second note from the customer section

April 12, 1993 11:54 AM

3va Per Square Foot X  1800 Square Feet ...........    5400

1500va Per Small Appliance Circuit X  5 Circuits ..    7500

1500va Per Laundry Circuit X  1 Circuits ..........    1500

Electric Range ....................................   12000

Cooking Unit Two ..................................    5000

Cooking Unit Three ................................    3500

Electric Dryer ....................................    5000

Water Heater            ...........................    4500

Dishwasher              ...........................    1500

Pool                    ...........................    1752

Fan                     ...........................     660

Pump                    ...........................     600

======

Total Other Load .................................:   48912

First 8,000 at 100%:                                   8000

Remainder at 40% .................................    16365

~~~~~~

Calculated Total of Other Load For Existing.......    24365

Larger of Heat or A/C = Cool for a Demand Load ....    4500

======

Total Load for an Existing Dwelling ..............    27365

Minimum Calculated Service Size =  27365 Watts � 240 Volts =  114 Amps.

Service Information

~~~~~~~~~~~~~~~~~~~

Service Request #.. NH10355

Square D 200 Amp 40 cir Main Breaker

4/0 AL Type XHHW in 2" PVC

#6 to Copper Ground Rod & Water Piping

18 - Spare Breakers

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 13

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

HELP SYSTEM

The help system is a Context Help System and Hyper-Text Help

System.  Some help screens have Hyper Links that relate to the

subject in discussion.

THIS IS THE CONTENTS SCREEN

<Square Feet>            <Cooking>            <Electric Heat>

<Small Appliance>        <Heating>            <Continuous>

<Laundry>                <Cooling>            <Four or More>

<Fixed Appliance>        <Motor Loads>        <Service Info>

<Customer Info>          <Note>               <Service REQ#>

<Reports>                <Data Base>          <Help on Help>

<Command Buttons>        <Service Schedule>   <Formulas>

<Demand Calculation>  <Special Keys>  <Maximum Field Length>

<Database Repair Utility>         <Database Packing Utility>

F1 =    Pressing the F1 key on any field will bring up context help.

-----------------------------------------------------------------

SELECTING A HELP LINK

With a MOUSE - Click on phrases outlined by two triangles. With the

keyboard Press TAB or Shift-TAB to select a link. Press ENTER to

jump to that topic.

-----------------------------------------------------------------

SCROLLING THE HELP WINDOW

With a MOUSE     - click on the horizontal or vertical scroll bars.

With KEYBOARD    - press the cursor navigation keys.

-----------------------------------------------------------------

CLOSING THE HELP WINDOW

With a MOUSE  - Double click on the window's control box icon. top left.

With KEYBOARD - Press Esc or Ctrl-F4.

Contents      - Displays a Table of Contents for the application's

HELP. Press C to select Contents.

Search        - Opens a dialogue box that lists all available HELP

topics.  Select a topic from the list box and press

ENTER. Press S to select Search.

Back          - Jumps to the last HELP topic viewed. Press B to

select Back.

History       - Lists the last 20 HELP topics viewed. Jump to a

topic by selecting from the list box and pressing

ENTER. Press T to select History.

Copy          - Copies the contents of the current HELP topic into

an edit area. Select the text you want copied to

the Clipboard and choose Copy. Choosing Copy

without selecting any text in the edit area copies

the entire HELP topic to the Clipboard. Press P to

select Copy.

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 14

RESIDENTIAL ELECTRICAL REPORTS.  DEMAND 2.0

SUPPORT

BY PHONE:

Monday thru Friday 9:00 AM to 5:PM Eastern Standard time call

(603)-893-9008

BY FAX:

24 hours a day 7 days a week call 603-893-9008

BY MAIL:

Send your questions to:

Electrical Design Software

12 Vassar Drive

Pelham, NH 03076

Thank you for purchasing a software product from Electrical

Design Software. We are dedicated to producing electrical software

for the professional marketplace.

-----------------------------------------------------------------

(C) COPYRIGHT 1992-1993 ELECTRICAL DESIGN SOFTWARE      Page 15

#