Note: you can load this file into your favorite word processor.

---------------------------------------------------------

PowerSIZE/RES 2

Residential Load Sizing for HVAC Contractors

----------------------------------------------------------

Contents

Section

1   PowerSIZE/RES: Introduction

2   PowerSIZE/RES: Installation

3   PowerSIZE/RES: Tour

4   PowerSIZE/RES: Take-Off Tutorial

5   PowerSIZE/RES: Design Considerations

Appendices

Appendix  A

License Agreement

Disclaimer of Warranty

Appendix  B

U-Value data

Appendix  C

Climate data

PowerSIZE/RES Computer program and manual copyright (c) 1993 by

D. L. Hughes

.  All Rights Reserved. Mailing Address:  Post Office

Box 1671, San Jacinto, CA  92581-1671

Support policy: Due to the technical nature of this program, we

only offer Shareware support by mail at the above address.  Be

sure to include your phone and/or fax number number in all

communications. Be sure to include area code.  CompuServe users may

contact us at 72630,776.

1

PowerSIZE/RES:  Introduction

One of the greatest problems these days for heating and air

contractors is properly sizing equipment.  The reason this is

true is that they have often relied on "rules-of-thumb" to do

residential design work.

"Rules-of-thumb"

But times are changing and the old "rules-of-thumb" are not what

they used to be. Increased insulation, higher performance glazing

products, greater HVAC equipment efficiencies and other factors

are making many of the old rules obsolete.  Dwellings are

becoming more energy efficient and as a result equipment

requirements are not as great.

Too often HVAC contractors are interested in knowing only the

heat loss or heat gain for a dwelling before they make equipment

selection.  These numbers are not adequate to design a system.

In addition to BTU's, designers also need to know CFM's.  The

movement of air is just as important, sometimes more so, than the

heating or cooling capacity of a given piece of equipment.

Science or art?

It's assumed that the person using this program has a background

in HVAC design. Some people like to think that systems design can

be reduced to a pure science, but that's not really the case.

It's an art, too, and experience is an important factor.  This

program will inform your understanding of the thermal dynamics of

a dwelling, but is just one factor in the systems design process.

What else must you know?  It's important that you have a handle

on the range of equipment available, duct layout methods

(including what pressure drops due to air delivery) and

procedures for a good system installation.  The best design in

the world will not help if the system is not properly installed.

In addition there are more mundane things, like the preferences

of the dwelling owner or architect and the amount of money in the

budget.

Verify work

If you use this program and find things that are different from

your experience, it's important that you call program support

line to discuss the matter, or consult with a local mechanical

engineer. Run a few sample jobs to develop an awareness of how

that pro- gram operates, and features that will cause your

numbers to vary widely before relying on the program.  For

example, the cooling BTU's always seem low until someone figures

out that it always comes out "just right" if you drop the summer

inside design temperature down to 74 degrees F.  The only problem

with doing that is that California regulations required that

setting to be left at 78 degrees F!  You need to check to see if

your local jurisdiction has a special interior design temperature

which you are required to use.

Of course this program will be used under a wide variety of

conditions and because of that, you, as the user, are responsible

to make sure values are correct and that the results are applied

in a professional manner.

An Important tool

We think you'll find PowerSIZE/RES a very important tool.  It

will give you the informa- tion you need to size equipment and

design a system.  Based on the  information it provides, you'll

probably be formulating a whole new group of "rules-of-thumb" to

apply to modern, energy-efficient dwellings!

NOTE: Page numbers shown apply to printed manual only.

2

PowerSIZE/RES:  Installation

In this section we'll learn how to install the program on your

computer.  Then, we'll also install your company name and the

model printer you're using.

Before we get started, make sure your computer meets minimum

systems requirements:

IBM(tm) or compatible

DOS version 3.2 or greater.

A hard-drive with a minimum of a half-megabyte of space

available.

TIP: you can run this program off a 720k or larger floppy drive,

but it's not recommended because of speed considerations. If you

do want to run it off a floppy be sure that you boot the computer

in such a way that the CONFIG.SYS has the proper number of FILES

and BUFFERS in it.  The program will not run unless these are

properly set a boot-up time.  See below for details.

Any monitor, color or monographic.

Any printer.

Are you ready?

Step 1: Create a new hard-drive subdirectory called SIZE (or any

name you desire).

Step 2: Insert either 5.25 or 3.5 distribution diskette in the

appropriate drive (usually A: or B:).

Change the prompt to the appropriate drive (by typing A: or B:,

then <Enter>.  At the proper drive prompt type:

> copy *.* c:\SIZE   (or whatever you named the new subdirectory

you created).

Change back to the SIZE subdirectory, then unzip the program in

the usual way:

> PKUNZIP psrBTU.ZIP

TIP: If you need to set FILES and BUFFERS manually, you may do by

using Copy Con, Edlin, or a text editor to change the CONFIG.SYS

settings.  For details on how Copy Con and Edline work, consult

your DOS manual.  Here are the settings you need: FILES=40

BUFFERS=30

After the installation, you are ready to enter the program by

typing

> PSR

at the prompt in the newly created SIZE subdirectory created by

the installation program.

Company/printer installation

Immediately upon typing PSR you find yourself at the "welcome"

screen.  Look it over this first time, then press any key to

continue.

The next screen you see is the "legal" screen.  Please read it,

along with the program license and disclaimer of warranty that

appears in Appendix A of this manual.  Press any key to continue.

After the "legal screen" is the "beg screen".  This is a serious

piece of software, and you are required to register it if you use

it beyond a brief evaluation period (like one job). The

registration fee is only $99.  For this fee you get a complete

manual, the ASHRAE weather data for your state or provience, and,

of course, a copy of PowerSIZE/RES without all the promotional

screens.  You can register your copy of PowerSIZE/RES by sending

your check for $99 to:

D.L.Hughes

Post Office Box 1671

San Jacinto, CA  92581-1671

End of commerical.

Now you find yourself at the MAIN MENU.  Immediately use the

<RightArrow> key (or press the highlighted letter <U> and enter

the Utility option.  The first thing you'll want to do is press

<I> for installation.

Enter all your company data, as much of it will appear on later

reports.

After you exit the last piece of company data, the fax number, a

pop-up scrolling pick window will appear.  You'll be seeing many

of these throughout the program, so we'll take a minute here to

discuss how they all operate.

"Pick" windows

When such a window appears it is filled with data.  You may use

the <UpArrow> or the <DownArrow> to scroll through the data to

find the item you want.  Once you find what you want, press

<Enter> to select (or "pick") the item you can to input.

All such windows have an alternative way of finding things.

Instead of using the arrow keys, you may simply start typing the

letters of the name of the item you're searching for and the

program automatically searches for the item.  For example, the

first printer shown in the selection screen is the Citizen MSP

10, but you want to install an IBM Proprinter XL.  Type the

letters <I> <B> <M> at the top of the selection screen and the

cursor will move directly to the first of two IBM printers

available.  You can then use the arrow key to move you down one

line to the XL model.

If your automatic search is unsuccessful, a tone will sound.

Press <Esc> and start your search again.

TIP:  To overcome bad searches because of typing errors, just

press the first letter in the word you're searching for, such as

<I> in IBM, then use the arrow keys to move to the exact item you

want.

Remember, this search method works on all scrolling pick windows,

such as the climate data window and all the U-value windows.

More about Printers

As you see, in the printer pick window you can select from among

21 different brands and models of printers.  If you have a

printer which is on the list, select it.  If your printer does

not appear, don't worry.  Virtually all dot matrix printers have

an Epson emulation and you should select an Epson model that

works with your printer.  Check your own printer manual for

details.

If you are using a laser printer which is not listed, try the HP

LaserJet II installation. Most laser printers have an HP LaserJet

II emulation.  Again, please check your printer manual for

details about how the emulation works with your printer.

You may need to experiment a bit if your printer is not among the

printers listed. If you have problems, call us and we'll advise

you, perhaps even send you a special printer driver if required.

It has been our experience, however, that special drivers are not

needed because of the Epson/HP LaserJet emulations.

Once you have completed company and printer data, the

installation process is completed.

3

PowerSIZE/RES:  Tour

Let's take a quick tour through the program to acquaint you with

the data that goes in each field.  This tour will be of the most

help if PowerSIZE/RES is up and running on your computer screen.

To start the tour, go to the MAIN MENU. If you're still at the

installation screen press <Esc> twice to get there.

TIP:  If you get "lost" in the program you can always press

<Esc>, several times, to get back to the main menu.

If you're just starting the program, press <Enter> twice to get

to the main menu.

We're going to look at each main menu option:

Job file

Use the arrow keys or press <J> to enter the job file.

You now find yourself at the job file menu and you can add or

edit a job.  Press <A> and let's explore how to add a new job.

The job data screen appears and you may input data into the

following fields.  You may not want to actually complete a job

right now, but just "enjoy the sights" as each feature is

explained on this tour.

Owner: Input owner of the job you are sizing.

Job address:  Input the job site address.  If you are unsure,

input parcel number or some other specific identifier so you

won't confuse this job with another one later.

TIP:  The job address is what is known as a "key field".  That

means you will not be allowed to add the same address twice.  If

you try to do so, you'll get an error message.  You can edit any

address as many times as you like, of course, but you can only

add an exact address once.  If you find you must do more than one

calculation at the same address, change the address just a

little.  For example, your first run might be "1234 Oak Street".

Make the second run "1234 Oak Street-2" to avoid conflicts.

City:  City where job is located.

Description: Input a brief description of the job.  Sometimes you

may want to say something like "3 bedroom and den" or you may

want to describe the type of equipment you expect to install,

like "5 ton unit downstairs".  The description is a reference for

your own needs.

Date:  Your computer system date will automatically appear here.

You may change the date if you desire.

Job Data Screen

After exiting the Job Data screen, the program immediately takes

you to the Climate Data/Design Data screen.

TIP: If you want to go back to the Job Data screen, press <PgUp>.

To return back to the Climate/Design screen, press <PgDn>.

IMPORTANT NOTE: In the Shareware version of this program, we have

input one key city for every state in the US and every province

in Canada.  Proper HVAC design dictates that you use the actual

climate data for a site closest to your job.  So, the climate

data provided in the Shareware version is for demonstration

purposes only.  The data is valid, but only if your job is very

near one of the cities listed.  When you register your copy of

PowerSIZE/RES, you'll get more complete ASHRAE climate data for

your state or province.

Location:  You must select a "climate data city location" in

order to do the sizing calculations.  Press <F2> and a scrolling

pick window of locations will appear.  Use the automatic search

function described in the installation section or the <UpArrow>,

<DownArrow> to find the city which is nearest your job site.

Once found, press <Enter> to input the city you have selected.

All the climate data related to that city will automatically

appear on the screen when you select it.

Fields which are automatically filled for you when you select a

city:

Latitude: From ASHRAE data.

Winter Outside Design Temperature: From ASHRAE data.

Summer Outside Design Temperature: From ASHRAE data.

Summer Range: From ASHRAE data.

You must pick a climate data city in all cases.  If you do not

select the city nearest your job site, then all calculations will

not be effective.

TIP:  It's a bad idea to just type in location data into this

screen in a random way. Incorrect data will cause inaccuracies in

your sizing results.  It's always best to "pick" data as

described above.  You can input special weather city data you

want under the "Climate" section of the main menu.  Later, we'll

be discussing that menu option in detail.

Number of bedrooms: This is used to figure the "people load"

which is distributed by the program throughout the dwelling.

Basically the program multiples number of bedrooms x 2 people x

225 BTUH's per person.

Location of ducts:  The default setting is "attic".  If your

ducts are elsewhere, press <F2> and you have the choice of

inputing either "Conditioned" if ducts are in conditioned space

or "mixed" if ducts are in mixed locations such as in attic,

basement or conditioned space.  If most of the ducts are in the

attic, leave it at that setting.

Face velocity: You have the ability to set the velocity of air,

in feet per minute (FPM) that comes from a register.  The default

setting is 500 FPM, and the register make be too noisey if set

higher.  Some designers set the FPM lower, such as 400-450 FPM.

Heating Supply Temp:  This is an important number because it

affects your CFM calculation.  You must input the actual

temperature of the air leaving the furnace.

TIP:  This temperature is sometimes found in product literature,

though you may have to call your supplier and ask.  Of course you

can always stick a thermometer in an existing using to find the

temperature.  Remember, however, that you must measure the

temperature immediately as it leaves the heat source, not any

distance away.

The default heating supply temperature is 130 degrees F, and you

may find that most heating units are very near this figure.  The

more accurate this input is, the more accurate your CFM

calculation will be.

Cooling Supply Temp:  Again, this number affects the accuracy of

your cooling CFM's. Find the temperature in product literature,

by calling your distributor or by using a thermometer on an

existing unit.  The default for temperature is 55 degrees F, and

you may find that most cooling units are very near this figure.

Latent Load Fraction: Set to .20 for dry climates or .30 for

humid climates.

Infiltration: Default set to medium, and this is the best setting

for most dwellings.  The "pick" window pops-up automatically and

you may change this setting to "loose" if it's an old dwelling

and there are strong drafts around windows or doors. You may

change the setting to "tight" if the dwelling is new and special

infiltration barriers have been installed.

Winter Inside Design Temperature:  This is another very important

number.  Some states, like California have set inside design

temperature by law.  It is 70 degrees F in California and needs

to be left at that figure.  This is a good number to use, though

you may want to check to see if your state has another

requirement.

Summer Inside Design Temperature: Again, this is a very important

number.  In California the default is 78 degrees F and needs to

be left at the number in that state.  If you are using this

program in a state other than California, check the regulations

for a different requirement. In the HVAC industry the 78 degree

inside design temperature is not popular since hardly anyone sets

their thermostat that high and equipment may be undersized on a

BTUH basis alone.  Many industry people prefer a 74 degree summer

inside design temperature and that is a good number to use unless

regulations do not allow it.

After entering the last item, the program automatically takes you

to the Room Data Menu.

TIP:  When at the design data screen you press <F2> to select the

climate city location. Then go down and add the number of

bedrooms by either pressing the <Enter> or <DownArrow> key four

times.  If you're satisfied with all the other default inputs

after inputing the number of bedrooms, just press <PgDn> at that

point and you'll automatically come to the Room Data Menu.

Room/Zone Data

Now, at the Room Data Menu, press <A> to add room data.

Individual Room/Zone: Input the name of the room you want to

size.  Instead of a specific room, you may want to input the name

of a zone.  Both methods are explained in the tutorial section of

this manual.

TIP:  You may occasionally want to do sizing for a whole house.

It's easy to do.  Just input HOUSE in the room/zone field and

input whole house totals into the various fields that follow.

Conditioned Floor Area:  The CFA is another important number.  It

is the square footage of the actual space being heated and/or

cooled.  Sometimes a set of plans will show a gross square

footage which includes garage, porches and patios.  This is not

the number that is important to you.  You want only the net area

that is being heated or cooled, the area known as the

"conditioned floor area".

Average Ceiling Height:  The height, in lineal feet, from floor

to ceiling.  For cathedral ceilings take the high and low and

average the two.

Slab perimeter:  There are two components to the slab perimeter.

Of course if you are dealing with a house that has only a raised

floor, you can skip these inputs.  The two components for slabs

are length, in lineal feet, and the actual F2-factor. Key:

F2factor1 = Hard surface in rooms along perimeter of dwelling.

F2factor2 = Covered surface (carpet, cupboards, etc) along

perimeter. F2factor3 = Perimeter of house touches garage, porch,

patio, covered F2factor4 = Perimeter of house touches garage,

proch, patio, exposed

Input the perimeter of each type in lineal feet.  If there is no

slabedge insulation used, then leave the F2 factors at the

default shown.  If slabedge insulation is being used, then

consult the chart in Appendix B and use the appropriate number

from it. Note: these charts don't appear well on a computer

screen.  You're going to need to register your program to get the

printed manual where Appendix B appears.

Roof/Ceiling SF: Square footage of roof/ceiling assembly of

room/zone goes in first field. This is commonly the square

footage of the house in a single story dwelling.  You may have to

measure from plans in multiple story dwellings.  The U-value of

the roof/ceiling assembly goes in the second field.  Press <F2>

to pop-up a selection of assemblies from which to select.  If you

do not find a match, consult Appendix B.

Raised Floor SF:  Square Footage of raised floor in this

room/zone if any.  Remember this area counts only if one side of

the floor is in conditioned space and the other side is in

unconditioned (ambient) space.  Do not count area of floors where

the space is conditioned on both side of the floor, such as is

common in two story houses.  The second input is for the floor

U-value.  Press <F2> to select from scrolling pick window.

Consult Appendix B if you cannot find the assembly you need in

the pick window.

Skylights:  There are three parts to the skylight input.  First

is the area of skylights in the zone in square feet; second, the

U-value (press <F2> for selection); third, the shading

coefficient of the skylight <again, press <F2> for selection).

If you do not know if the skylight has shading leave the default

number at the 1.00 shown on the screen.

Number of Appliances:  Used to figure appliance heat gain in this

room/zone.  Include all major appliance is the zone.  Be sure to

count range and oven as separate appliances even if they are one

unit.  Count dishwasher, washer and dryer, refrigerator and

freezer if in conditioned floor area.  Ignore small appliances

like garbage disposals, toasters, etc.

Now we come to the vertical surfaces section for this zone.

The cursor automatically moves into this area, and you must press

<RightArrow> to pop-up the orientation pick window. When the

window appears, select the orientation by moving the light bar to

the desired azimuth and pressing <Enter>.  You may correct an

entry by pressing the <UpArrow> and making another selection.

Note: do not just type in an orientation.  Always use the pick

window to select.

Wall Square Footage:  Input area of net wall of room/zone for

this orientation.

Wall U-value:  Press <F2> to select wall U-values.  If you cannot

find a value to match the walls shown on the plans, consult

Appendix B.

Fenestration (Glazing) Square Footage: Input area of glass of

room/zone for this orientation.

Fenestration U-value: Press <F2> to make selection.

Fenestration shading coefficients:  If window has a shading

device, like drapes or blinds, press <F2> and make selection.

TIP:  Including shading coefficients will severely reduce cooling

load.  If you are unsure of the shading devices that will be

used, or that owners will open and close them at the proper time

each day, or if you think the window coverings might be changed

by new owners at a later time, it is best to leave the shading

coefficient at the 1.00 default.

You have just completed a room/zone and are back at the Room Data

menu.  If you want to add another room/zone to this dwelling

address, press <A> to add.  Repeat this process for each

room/zone.

TIP:  Repeating this process is not as tiresome as it may seem.

The U-values you input for this house are retained, so all you

have to do is change those U-values that apply.  Of course you

must input measurements for each room/zone, but that data is

quickly available from your take-off sheet as explained in the

tutorial section.

If you need to edit any room/zone in this dwelling, press <E> at

the Room Data Menu. If you have finished all inputs, press <Esc>

to return to the Job File Menu.

If you want to edit a job file, press <E> and you'll find

yourself at a scrolling pick window which shows job address and

description. Move to the job you want, then press <Enter> to

select.  Note: This edit selection screen is the only place in

the entire program where you can delete a job.  To do so, move

the lightbar to the job you want to delete, then press the <Del>

key.  Be careful, the deletion is permanent!

When you are in edit mode you can move through the screens in the

same way as described for the "add" mode described above.  If you

get "lost" you can always press the <Esc> key repeatedly until

you get back to the Main Menu.

Back at the Main Menu

We've just gone through the process of inputing dwelling data for

sizing.  The next thing that you may logically want to do is

print the sizing report.  To do so, press <R> at the Main Menu.

Report Option

NOTE:  There may be a difference in totals between the Room-by-Room

report and the Heating and/or Cooling reports.  This is because two

different menthods are used to arrive at the same numbers.  Also, the

rounding of numbers has a slight influence.  If totals are off

more than a few hundred BTUH's, go back to room-by-room menu and move

the cursor through the entire screen of one room of the dwelling.  This

process serves to "force" calculations, and the totals of the two kinds of

reports should be very similar.

Upon pressing <R>, another pick window appears, and you select

the job you want to print by address.  Press <Enter> to select

the highlighted address and another menu appears.  You may send

the report to either the screen or the printer.  Make your

selection, then wait a few moments while the report is processed.

Climate Option

The climate data is in a separate database which is accessed by

pressing <C> at the Main Menu.

Here you see all the design information which is needed to size a

dwelling.  Happily, you can ignore all this if you desire because

the relevant information is automatically input into the

PowerSIZE/RES when you select the climate location city.

*** NOTE: The following options ares not available in the

Shareware version.  In the Shareware version you are limited to

the selected cities, one for each state and province. When you

register your copy of PowerSIZE/RES you will receive more

complete climate data for your state or provience.

However, you may want to add, edit or delete climate information,

and this is the spot to do it.

ADD: To add information, press the <Ins> key.  Be sure you have

ALL the information you need when adding a climate location.

This information is available from ASHRAE or other sources.

WARNING: if you input wrong or incomplete information here, you

will get wrong or incomplete load sizing calculations!

EDIT:  To edit information, highlight the line you want to

change, then press the <RightArrow>.  Move the cursor to the item

you want to change and change it.  Press <Enter> as many times as

you need to get to the end of the line.  The change will be

automatically saved.  WARNING: Be sure you are making the change

for valid reasons. Wrong or incomplete information will result in

wrong or incomplete load sizing!

DELETE:  To delete a climate location, highlight the city then

press the <Del> key. This will permanently delete the highlighted

city.  NOTE: Sometimes people think they are saving disk space by

deleting cities they don't use.  Usually this is false economy as

it is very desirable to have all the locations instantly

available when you want them.  It's a better idea not to delete

any climate locations in the database. To leave the climate

location database, press <Esc> and you'll be back at the Main

Menu.

Utility Option

If you read the installation section of this manual, you have

already had a brief look at the utility option.  If you have not

done the company and printer installation, please go back and

read section 2 now as we won't repeat that data here.

NOTE: "File maintenance" is a "cure-all" for most data problems.

Please read the next paragraph carefully!

File maintenance: The file maintenance option automates the

purging and reindexing of program files.  If you are using the

program heavily, do a file maintenance weekly.  You will also

want to use this option if your data files get "corrupted" for

any reason, like a power loss.  In fact, file maintenance is kind

of a "cure all".  If you experience any problems with "lost"

data, failure to print, etc. do a file maintenance and you'll

probably find that every thing has been set right.  To do a file

maintenance, just press <F> and the program does all the work.

DOS Services:  In the PowerSIZE/RES program and need to run

another program or use some DOS command?  All you have to do is

press <D> and you find yourself at a DOS prompt.  Go ahead and do

what you need to do.  After exiting the other program, or

executing a DOS command, type EXIT and you're back in

PowerSIZE/RES.

Now back to the Main Menu.

Quit Option

Always quit PowerSIZE/RES in an orderly way.  That is, don't shut

off the machine in the middle of a session, but instead go to the

main menu and press the <Q> key.  By doing so you'll close out

the program in the proper way and get a nice final message on the

screen telling you the exit was normal.

If you don't see the message it means the exit was not normal.

In that case run the program again and IMMEDIATELY go to the file

maintenance option in the utility menu.  This will restore data

that might have been lost by a disorderly exit.

Well, that's the end of your guided tour.  Hope you enjoyed the

trip!

Data Backup Procudure

It's important that you backup your data files often as insurance

against data loss.

To backup your files use the DOS "COPY" or "BACKUP" commands to

archive the all files with *.DBF and *.NTX extensions.  An

example using the "COPY" command:

C:\> Copy *.DBF A:

wait until files have been copied from C: to A:

C:\> Copy *.NTX A:

wait until files have been copied from C: to A: Backup complete.

If you have questions about the DOS "COPY" or "BACKUP" commands,

please consult your DOS manual.

4

PowerSIZE/RES:  Take-Off Tutorial

In this section we'll discuss the procedure for doing a sizing

calculation.  We will focus on how to collect the data from the

plans to put into the program.

Once the data has been collected, then you can input it into

PowerSIZE/RES is the manner described in the previous section.

Your objective is to take a set of plans and collect data from

them in a fast and accurate manner.  To help you achieve this

goal there is a special plan take-off sheet at the end of this

chapter for you to photocopy and use.  We'll use this sheet and

the sample plan on the following pages to an actual take-off.

IMPORTANT NOTE:  As we do this take-off, we are only interested

in surfaces (walls, roofs, floors, etc.) where it is conditioned

space on one side and unconditioned (ambient) space of the other

side.  Your load calculations will be inaccurate if you include

any surfaces which are either conditioned on both sides or

ambient on both sides.

One Step at a Time

Step 1: Input "general data".  All of this data is

self-explanatory, except perhaps for the heating/cooling supply

temperatures.  These temperatures are discussed fully on page 11

of this manual.

Step 2: View the plans and see how your going to divide up the

rooms.  Note page 21 to see how we have done this.  Normally you

will want to do your take-off on a strictly

*** NOTE:  We provide you with special take-off forms to make the

job easier.  This take-off form is described below.  However, the

form does not reproduce well on the the screen.  You will receive

a copy of the special take-off form in your printed manual when

you register your copy of PowerSIZE/RES

Room-by-room basis, but there are times when you'll group areas

together.  For example, on page 21 we have lumped the kitchen and

family room together into Room 1 since it is one big space.  It's

true you'll only get one BTU and CFM load for this area, but it

will be easy to split the totals when you do your layout.

Another case of combining areas is Room 6, where bedroom 2 and

hall area are grouped together.  We need to account for all the

conditioned floor area in a dwelling, so sometimes it's helpful

to group areas like this, especially in a small house like our

example.  If you were dealing with a huge house where hall areas

might have their own registers, then grouping would not be

helpful.

TIP: Total the CFA (Conditioned floor area) on your take-off

sheet to make sure that it matches the figure shown on the plans.

It's easy to miss some portion of the dwelling, and when you do

your load calculations will not be accurate.  A simple comparison

of numbers will solve the problem.

Step 3:  Once you have decided how you're going to divide-up the

dwelling, list the Room # and the Room name on the take-off

sheet.  Then go systematically around the dwelling and write the

compass orientation.  That is, what direction a particular wall

is facing.  Notice our example, there is only one room (#7) that

faces a single direction. All the rest are corner rooms and face

2 different directions.

TIP:  You have a choice here.  One choice is to write down data

as we have here using a "/" mark to differentiate between the

various areas that apply to different orientation.  That is, we

have shown there is a gross wall area of 176 SF facing south, and

120 SF facing east. This is a quick and easy way to gather the

data when a house is small.  However, when a house is large, you

may want to have a separate line for each orientation.  An

example:

Room      Facing Room #   Name      NSEW

1        Kit/Fam     S 1a       Kit/Fam     E    .... and so

forth.

This method makes complex projects clearer, and is just as easy

to use when you input data into PowerSIZE/RES.

Step 4:  Next determine the square footage of each room or

grouping and write it in the appropriate space.

Step 5:  Determine the ceiling height of each room.  Most rooms

are eight feet tall, but you should consult the section plan (see

page 20) to see if some ceilings are higher. Note that in the

case of our example the living room is the only room that has a

ceiling higher than eight feet.  It is eight feet on the low side

and twelve on the high side, so we're going to call this average

ceiling height ten feet.

Step 6:  Next is the slab perimeter data.  On the take-off form

we have written down 22 lineal feet of exposed slabedge in the

Kit/Fam area, and since there is no slabedge insulation in this

house we have put a "D" down for "default", the value already

input into PowerSIZE/RES.  If slabedge insulation is used on your

job, consult the last page of Appendix B for the correct value.

You would write down that value instead of a "D".

The Kit/Fam area also has 15 lineal feet of covered slabedge, the

length of wall covered by cabinets.   The example shows all the

other perimeter is covered by carpet.  Even though the living

room is covered by carpet, we applied 22 feet of its length to

SP3 because it adjoins the garage.

Step 7:  Roof areas in a single story house match the room area.

We just wrote "R-30" as a notation for ceiling insulation and

will select the exact value from the "pick" window when we input

the data into PowerSIZE/RES.

Step 8:  In our example, there is no raised floor so we have left

these columns blank.  In most cases the area would be the same as

the CFA.

TIP: One of the places where raised floors are commonly missed is

the slab-floor house which has a room over the garage.  Since the

garage is ambient space (if it has no registers), the floor above

is "raised".

Step 9:  Skylight square footage, U-value and shading

coefficient.  Our sample house has no skylights, but if it did

we'd include the appropriate values in the three spaces allowed.

If your project has skylights, remember to subtract their total

square footage from the roof total for the room.

Step 10:  Number of appliances.  Input the number of major

appliances found in the room.

TIP: PowerSIZE/RES automatically distributes heat gain from

people to rooms throughout the dwelling.  However, the heat gain

from appliances stays with the room where you input them.  If you

want to distribute appliance gain to other rooms, just input a

number in the room where you want the gain to show.  Never input

more appliances in rooms than the house actually contains.

Step 11:  Input room wall square footage (length x height) on the

appropriate line.  Be sure to subtract fenestration area to get

net wall area.  Yes, this is in reverse order on the form, but we

wanted the form laid out in such a way that it would be easy to

use data from it to input into PowerSIZE/RES.   Sorry, we just

couldn't have it both ways!

Write down the wall U-value as it appears on the plans, then pick

the exact value from the "pick" window when you input it into

PowerSIZE/RES.  By the way, give the section plan a good look as

sometimes the wall insulation value changes from wall-to-wall.

Step 12:  Next, write down fenestration (glazing) totals, along

with the U-value of the glass.  Fenestration shading, such as

drapes or blinds, cause special concerns for HVAC contractors

since the devices are often not open and closed at proper times

by homeowners.  We have shown no interior shading devices in our

example.  See page 14 of this manual for a more complete

discussion of whether or not interior shading devices should be

added to a dwelling for sizing purposes.

That's it!  Now you are ready to input this information into

PowerSIZE/RES!

5

PowerSIZE/RES: Design

Considerations

PowerSIZE/RES calculates BTUH's and CFM's for each room, and

provides the free space required, in square inches, for registers

in each room.  Once you have this information in hand, it's easy

to design a system.

The program makes a number of assumptions, and we'll cover some

of them here, and also give some tips for good design.

Ducts and Registers

It's assumed that the room you have input will have a register,

and optionally a return air grille.  If a space does not have a

supply, then you'll want to combine it with a room that does.

Return air grilles should be one size larger than the supply

register.  If you have a central return air, be sure to that all

doors are undercut so air will flow freely back to the source.

Anytime PowerSIZE/RES calculates a room as having less than 50

CFM, the lower number is over-ridden and 50 becomes the minimum.

The 50 CFM minimum is important because air will become stale if

it's not moving at least at this volume.  This is particularly

important for bathrooms.  You may want to adjust CFM's in other

rooms as well.

You must evaluate total CFM because the total of man CFM

minimums may mean larger ducts as well as throwing you into the

next largest equipment size.  This may be counterproductive from

a cost standpoint, so you may want to use the small equipment an

scrimp a bit on CFM's in areas where impact will be small.

If heat loss exceeds 10,000 BTUH in a given room, use more

than one supply.  Do this also in rooms with large non-north

facing windows.

PowerSIZE/RES computes register free space based upon a face

velocity of 500 FPM.  You can use this number as a guide when

selecting registers, as free space is one of the selection

criteria which appears on most product specification sheets.

There are other considerations when selecting registers: pressure

loss (normally 0.1 Inches of Water for duct run of less than 100

feet, 0.05 for runs greater than 100 feet.) and "throw".  The

horizontal throw of air should ideally be 3/4 the distance across

the room from the register.

To reduce drafts in smaller rooms, increase register to the

next larger size.

Once PowerSIZE/RES provides you with CFM's by room, use an Air

Duct Calculator (provided free by most HVAC equipment

manufacturers) or chart (see next page) to determine duct size.

Select "Friction per 100 Feet of Duct" (0.1 for most residences)

and match it with the CFM for the specific room.  Then, note the

"Round Duct Diameter".  For example, if the Friction is 0.1, the

CFM is 100, the round duct size would be 6 inches in diameter.

Use the chart on page 29 to translate round duct diameter to

rectangular ducts, if needed.  Note: Chart not available in

Shareware version.

When sizing a duct system, always start at the supply

register which is the greatest distance from the HVAC unit, then

work back to the unit.  This duct will remain the same size until

it joins a larger duct.  That duct will increase in size based

upon how many smaller ducts join it.  If there any chance that

cooling will be installed, always size ducts to accomodate it.

Heating/ Cooling Equipment Selection

Equipment efficiency is of growing importance in these days of

ever-increasing energy costs.  The higher the efficiency (AFUE

for heating, SEER for cooling), the less energy costs will be for

homeowners.  Everyone today ought to be selling the highest

efficiency equipment possible.  The only problem with this is

that high efficiency equipment is more costly, and the job will

probably go to the contractor who bids cheap, minimum efficient

equipment.  Wise contractor's will sell the benefits of high

efficiency equipment to their clients, as "value" is more

important that "cost".

When selecting a furnace remember that peak OUTPUT of the unit

should never be less than the heat loss of the building.  But

BTUH's are just one part of the issue; also be sure the furnace

has adequate CFM's.

Along with CFM's you must consider pressure drops to determine

if you have adequate fan volume.  The static pressure of the unit

fan must equal or exceed the system pressure drops.  How do you

figure pressure drops in a system?  Here are some typical

numbers:

Return air inlet        0.05

Filter when dirty       0.10

Cooling coil            0.20

Supply outlet           0.05

Duct pressure drop      0.10*

Total      0.50

This means the furnace you select must be able to provide at

least the total CFM shown by PowerSIZE/RES at this total external

static pressure, though you'll probably want to select the next

size up rather than depend on the unit working properly at it's

minimum performance standard.  Note: If computed external static

pressure is not shown in furnace product literature, select the

next larger pressure shown.

If the CFM is too high at the required external static pressure

(causing noise and excessive drafts), install a damper and adjust

it to the proper CFM.

* To figure the exact duct pressure drop use this equation:

Inches of Water = Length of longest run (lineal feet) x 1.5 x  .1

/ 100

Example:   82 x 1.5 x .1 / 100 = 0.123 Inches of Water

Today, selecting an appropriate cooling unit (coil/condenser)

is much easier than in the past because manufacturers are making

companion units.  That is, a certain heating unit requires a

matching cooling unit.

If your job has cooling, be sure the coil CFM (at the correct

pressure drop) requirements and the volume of air available are a

match.

Always keep in mind that the configuration of the dwelling,

climate conditions, local regulations, the performance of

equipment from differing manufacturers and other elements can

affect system design and selection.  You are advised to consult

with general contractor, mechanical engineer, local building

officials, HVAC equipment distributor or any other required

professional before committing yourself to any specific design.

Appendix A

License and

Disclaimer of Warranty

License Agreement

Shareware version

Any vendor or individual is granted the right to distribute this copyrighted

Shareware version 1.A of PowerSIZE/RES as long as:

1) The complete program is included on all distribution disks.

2) Notice is provided that this is the Shareware version, and that if

the program is used beyond a brief evaluation period, registration and

payment of $99 fee is expected.

Registered version

This is a single copy software license granted by D.L.Hughes,

Post Office Box 1671, San Jacinto, CA 92581-1671.  The software

is licensed to you as the end user.  It is not sold.  You are

granted a nontransferable and nonexclusive license to the

original purchaser of PowerSIZE/RES  This program must be used

only on a single computer. Archival copies may be made by the

purchaser, but Federal law provides severe penalties for the

unauthorized reproduction, distribution or exploitation of

copyrighted computer programs.

Disclaimer of Warranty. This program is sold without any express

or implied warranty. Because of the diversity of conditions and

hardware under which the program may be used, no warranty of

fitness for a particular purpose is offered.  The user is advised

to test the program thoroughly before relying on it.  The user

must assume the entire risk of using the program.  Any liability

of seller or manufacturer will be limited exclusively to product

replacement or refund of the purchase price.

Appendix B

U-values of construction assemblies

NOTE: These charts are not avaiable in the Shareware version.

Appendix C

Climate data

Note: These charts are not available in the Shareware version.